# ForgeAI Conversation Review

FD Fan / ID Fan / PA Fan Performance Analysis — Tiroda Thermal Power Project

Conversation ID: a2bf118f-9c05-4e2d-967f-28a2bcf0b10f

Project ID: 21

Created: 2026-08-14T15:30:07.691657+00:00

Total turns: 24 messages (12 question/answer pairs)

Source: response-1.json + response-2.json (ForgeAI conversation export)

This document reconstructs a ForgeAI chat session for human review. Each question is followed by the agent's tool calls (the live data/document lookups ForgeAI performed to answer), its written analysis, and any charts it generated. Tool results are summarized/truncated for readability; full raw output is available in the original conversation export.

# Q1.  Show deviation of FD Fan performance from characteristics curve from base load and 60% load.

Asked: 2026-08-11T09:23:37.442304+00:00

ForgeAI Response

I can't answer this one from the corpus, and I want to flag why clearly rather than force a number.

The FD characteristic-curve deviation cannot be computed here — for two independent reasons:

No load reference for FD. FD/PA data is all December 2018; MW only exists in the ID tables (April/June/July). FD can never be joined to load — there is no "base load" or "60% load" operating point available for the FD fan data at all. The closest available load-like signal for FD is a proxy: total_secondary_air_flow (TPH) or <fan>_inlet_vane_position (%), and neither is MW.

The design duty table itself is compromised. Per the FD technical specification (§4.1.1), the design duty is organized as four conditions (TB, 100% BMCR, TMCR, 60% BMCR) across three coal grades, but as extracted:

The fourth flow group (375.2 / 366.0 / 358.3 m³/s) cannot be the 60% BMCR point — it exceeds the TB point (321.3–351.0 m³/s), which is full load *with margin*. I won't present it as the 60% duty or fold it into a range.

The inlet total pressure row has 9 values for 4 conditions — the mapping to conditions cannot be established from the extract, so I won't invent one.

Both need to be read from the original .doc, not the pre-extracted text, to resolve.

No characteristic curve is in this corpus anyway. The only characteristic-curve document referenced is for the Nagarjuna plant, which is explicitly a class-level reference, never a Unit-5 measurement. There is no curve to deviate *from* for Tiroda Unit 5's FD fans.

So a "deviation from curve at base load and 60% load" figure would require: (a) a load/MW signal joined to FD data — doesn't exist in this corpus, (b) a validated 60% BMCR design point — currently unresolvable from the extract, and (c) an actual Unit-5 FD characteristic curve — not present (only a different plant's curve exists).

What I can give you instead, if useful:

The FD fan's measured flow/pressure-proxy behavior (total_secondary_air_flow, dp_inlet_outlet, inlet_vane_position) across the full December window, described in absolute terms without claiming it against any duty point.

The defensible parts of the design duty table (TB and 100% BMCR flow ranges, pressure rise range 4,059–5,730 Pa, inlet air 50°C/27°C, density 1.018 kg/m³), clearly marked as spec values only, not compared to any measurement.

Would either of those be useful, or would you rather I flag this as a documentation gap (original .doc needed) and move on?

stop_reason: end_turn | tokens: {'input_tokens': 52787, 'output_tokens': 932, 'cache_read_tokens': 0, 'cache_creation_tokens': 0, 'total_tokens': 53719, 'model_call_count': 1}

# Q2.  How did FD Fan A Bearing Temperatures vary at multiple load points?

Asked: 2026-08-11T09:24:46.886696+00:00

ForgeAI Response

TOOL CALL 1: Forgeai Get Source Datasets [OK, 340 ms] Getting datasets for ForgeAI source 665 source_id: 665 search_word: chart1_fdfan1 Result preview: Dataset ID; Dataset Name; Schema Name; Dataset Type ID; Dataset Type; Dataset Path; Row Count Estimate; Data Volume Bytes; .... 3402219; chart1_fdfan1; fd_fan_data; 1; TABLE; 4299; .... Showing 1 of 1 row(s) returned. (Total Datasets: 1 ¦ Page: 1 ¦ Page Size: 10 ¦ Total Pages: 1)

TOOL CALL 2: Forgeai Get Dataset Schema [OK, 316 ms] Getting schema for dataset 3402219 from source 665 source_id: 665 dataset_id: 3402219 Result preview: Column ID; Column Name; Column Type. 14471; id; integer. 14472; row_seq; integer. 14473; reading_time_raw; string. 14474; reading_time; timestamp. 14475; furnace_lf_sd_olt_sa_flow; double. 14476; furnace_rt_sd_olt_sa_flow; double. Showing 6 of 73 row(s) returned.

TOOL CALL 3: Forgeai Get Dataset Column Profiles [OK, 682 ms] source_id: 665 dataset_id: 3402219 Result preview: Dataset Row Count: 4299 Dataset Column Count: 71 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count id¦integer¦Unique identifier for each row, ensuring traceability and supporting data integrity in analysis.¦AI Generated¦4299¦0¦4299¦No¦1¦4299¦2150.0¦¦¦¦26 (1), 29 (1), 474 (1), 964 (1), 1677 (1)¦26 (1), 29 (1), 474 (1), 964 (1), 1677 (1)¦¦0 row_seq¦integer¦Sequential row number, providing an additional index for data ordering or troubleshooting.¦AI Generated¦4299¦0¦4299¦No¦1¦4299¦2150.0¦¦¦¦14 [Truncated — 26,014 characters total]

TOOL CALL 4: Forgeai Execute [OK, 362 ms] source_id: 665 query: WITH banded AS ( SELECT total_secondary_air_flow, fdf_a_inlet_vane_position, fdf_a_inlet_air_temp, fdf_a_brg1_temp_1, fdf_a_brg1_temp_2, fdf_a_brg1_temp_3, fdf_a_brg3_temp_1, fdf_a_brg3_temp_2, fdf_ … row_limit: 10 Result preview: load_band:23; n:20; min_flow:701; max_flow:701; avg_flow:701; avg_vane:701; avg_inlet_air_temp:701; avg_de_temp:701; .... 1; 1433; 1016.03906; 1185.4375; 1097.412456748092; 23.252412479274295; 17.81981936782973; 56.04958446703884; .... 2; 1433; 1185.4375; 1367.71875; 1305.359028590382; 29.993222008304297; 21.733765841242143; 56.88340594198655; .... 3; 1433; 1367.78125; 1637.03125; 1504.1946553454393; 30.30876004591771; 21.20068309441731; 56.26943075294262; .... 3 rows; .... Showing 4 of 4 row(s) returned.

TOOL CALL 5: Forgeai Execute [OK, 327 ms] source_id: 665 query: SELECT corr(total_secondary_air_flow, (fdf_a_brg1_temp_1 + fdf_a_brg1_temp_2 + fdf_a_brg1_temp_3)/3.0) AS corr_flow_de, corr(total_secondary_air_flow, (fdf_a_brg3_temp_1 + fdf_a_brg3_temp_2 + fdf_a_brg3_temp_3)/3.0) … row_limit: 10 Result preview: corr_flow_de:701; corr_flow_nde:701; corr_airtemp_de:701; corr_vane_de:701. 0.0821195747310968; 0.0961504532926754; 0.8728023374669809; 0.3175372108219267. 1 row. Showing 2 of 2 row(s) returned.

### FD Fan A Bearing Temperatures Across Load Points

No MW/load signal exists for FD in this corpus — FD data is December 2018 only, and MW only exists in the ID tables (April/June/July), which never overlap with FD. In place of load, I'm using the defensible proxy named in the corpus: `total_secondary_air_flow` (TPH, plant-level secondary air flow, range 1,016–1,637 TPH) — say so explicitly rather than presenting it as MW.

Source: Power_Plant (source_id 665), table fd_fan_data.chart1_fdfan1, 4,299 rows, 23–26 Dec 2018, Fan A only. Bearing temps are averages of their 3 RTD elements: DE (drive end) = brg1_temp_1/2/3, NDE (non-drive end) = brg3_temp_1/2/3.

#### One-sentence answer

Fan A's DE and NDE bearing temperatures rise only mildly from the lowest to the highest secondary-air-flow band (DE: 56.0°C → 56.9°C → 56.3°C; NDE: 55.7°C → 56.6°C → 56.0°C), a swing of under 1°C that is well inside the RTD element's own noise, so flow/load has essentially no meaningful effect on Fan A's bearing temperature in this window.

#### Table 1 — Average bearing temperature by flow band (proxy for load)

| Band | Flow range (TPH) | Avg flow (TPH) | Avg vane position (%) | Avg inlet air temp (°C) | Avg DE temp (°C) | Avg NDE temp (°C) |
| --- | --- | --- | --- | --- | --- | --- |
| Low | 1,016–1,185 | 1,097.4 | 23.3 | 17.8 | 56.0 | 55.7 |
| Mid | 1,185–1,368 | 1,305.4 | 30.0 | 21.7 | 56.9 | 56.6 |
| High | 1,368–1,637 | 1,504.2 | 30.3 | 21.2 | 56.3 | 56.0 |

(1,433 rows per band, 4,299 rows total — collapsed to 3 bands rather than deciles, per convention.)

#### Table 2 — Individual RTD elements by band (°C), to show internal spread

| Band | DE-1 | DE-2 | DE-3 | NDE-1 | NDE-2 | NDE-3 |
| --- | --- | --- | --- | --- | --- | --- |
| Low | 57.7 | 55.8 | 54.7 | 55.3 | 55.3 | 56.6 |
| Mid | 58.4 | 56.6 | 55.6 | 56.2 | 56.2 | 57.5 |
| High | 57.8 | 56.0 | 55.0 | 55.6 | 55.6 | 56.9 |

#### Correlations (whole window, average metrics)

Flow vs DE temp: 0.08 (unrelated)

Flow vs NDE temp: 0.10 (unrelated)

Inlet air temp vs DE temp: 0.87 (very strong)

Vane position vs DE temp: 0.32 (weak)

#### Caveats

The band-to-band DE swing (56.0–56.9°C, 0.9°C) is smaller than the RTD element spread within any one band (e.g. Low band: DE elements 57.7 / 55.8 / 54.7°C, a 3.0°C spread). This confirms the corr result: flow does not meaningfully drive Fan A's bearing temperature here — the apparent bump at the Mid band is not resolvable from sensor noise.

Confounder tested, not assumed: inlet air temperature correlates 0.87 with DE temp — far stronger than flow (0.08) or vane position (0.32). Ambient/process air temperature, not fan loading, is the real driver of Fan A's bearing temperature swings in this window.

All values are well below the 90°C alarm / 120°C trip set points (same table in all three OEM manuals) — no action needed.

This is a 3-day historian chart export, a screening sample, not a continuous trend or degradation record.

If true MW-based load behavior is needed for FD, it isn't available anywhere in this corpus — only the ID tables carry MW, and they never coincide in time with FD data.

#### Chart

Bottom line: Fan A's bearing temperature does not meaningfully track flow/load in this window — the small band-to-band differences fall inside sensor noise, while ambient inlet air temperature is the dominant driver. Nothing here approaches alarm thresholds, so no action is indicated.

stop_reason: end_turn | tokens: {'input_tokens': 375654, 'output_tokens': 6855, 'cache_read_tokens': 240385, 'cache_creation_tokens': 0, 'total_tokens': 382509, 'model_call_count': 6}

# Q3.  What is the design duty of FD Fan?

Asked: 2026-08-11T09:33:29.810592+00:00

ForgeAI Response

TOOL CALL 1: Github Get Content [OK, 1879 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/extracted/Tech-Specs__FD_fan_technical_specification_Rev.A.txt Result preview: File: Tech-Specs__FD_fan_technical_specification_Rev.A.txt in sandhyatenneti/poc-power-plant Size: 107686 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/extracted/Tech-Specs__FD_fan_technical_specification_Rev.A.txt Content: ``` TIRODA THERMAL POWER PROJECT 1980 MW (2x660 MW Phase I + 1x660 MW Phase II) Tiroda, Gondia District, Maharashtra Forced Draft Fan Technical Specification REV.A Southwest Electric Power Design Institute September , 2009CONTENTS TOC \o "1-2" \h \z \u HYPERLINK \L "_TOC228282783" PART I Technical Specification PAGEREF _TOC228282783 \H 1 HYPERLINK \L "_TOC228282784" 1 General Condition PAGEREF _TOC228282784 \H 1 [Truncated — 107,173 characters total]

### FD Fan Design Duty — Tiroda Unit 5 (from FD Fan Technical Specification Rev.A, §4.1.1)

One-sentence answer: The FD fan design duty spans four load conditions (TB, 100% BMCR, TMCR, 60% BMCR) across three coal grades, with inlet flow ranging 239.4–351.0 m³/s and total pressure rise 4,059–5,730 Pa for the three defensible conditions — but the extracted 60% BMCR flow figures and the inlet-pressure mapping are corrupted and cannot be reported as-is.

Source: Tech-Specs__FD_fan_technical_specification_Rev.A.txt, §4.1.1 "Parameters of FD fan," explicitly marked in the document as tentative, pending APML approval.

#### Table 1 — FD fan inlet flow and total pressure rise, per coal grade

| Condition | Coal grade | Inlet flow (m³/s) | Total pressure rise (Pa) |
| --- | --- | --- | --- |
| TB (100% BMCR with margin) | Best | 351.0 | 5,730 |
| TB | Design | 342.4 | 5,624 |
| TB | Worst | 321.3 | 5,346 |
| 100% BMCR | Best | 292.5 | 4,407 |
| 100% BMCR | Design | 285.4 | 4,326 |
| 100% BMCR | Worst | 267.8 | 4,112 |
| TMCR | Best | 275.7 | 4,177 |
| TMCR | Design | 244.3 | 4,117 |
| TMCR | Worst | 239.4 | 4,059 |
| 60% BMCR | Best | 375.2 (flagged — see caveat) | 5,264 |
| 60% BMCR | Design | 366.0 (flagged) | 5,152 |
| 60% BMCR | Worst | 358.3 (flagged) | 5,040 |

#### Table 2 — Other design conditions (apply to all four load points)

| Parameter | Value |
| --- | --- |
| Inlet air temperature | 50°C (all conditions except TMCR, which uses 27°C per APML requirement — the designated fan performance test condition) |
| Air density | 1.018 kg/m³ (all conditions except TMCR/27°C case: 1.1205 kg/m³) |
| Sizing margin over 100% BMCR | 30% head, 20% flow (§4.3.19-A) |
| Best efficiency point | TMCR, design coal, 27°C ambient — the fan performance test condition |
| Curve deviation allowance | Flow 0 to +2%, pressure 0 to +2%, shaft power ≤2%, no negative efficiency deviation (§4.2.3) |
| Design-parameter deviation (fan sizing) | Flow ±15%, pressure ±5% (§4.2.17) |
| Stall margin | All operating points, full load to 20% load, must stay below the stall line (§4.2.4) |
| Single-fan coverage | One fan alone must cover 60% BMCR, best coal (§4.2.2) |
| Design life | ≥30 years (§4.2.1) |
| OEM model | FAF26.6-15-1 |

#### Caveats — read before using these numbers

The 60% BMCR flow row is provably wrong and I have not presented it as a usable design figure. 375.2 / 366.0 / 358.3 m³/s exceeds the TB row (321.3–351.0 m³/s), and TB is defined as "100% BMCR *with margin*" — i.e. the highest-flow, full-load condition. A 60% load point cannot have higher flow than 100%-with-margin. This is an extraction/table-scrambling error in the source document, not a real duty point. Do not use it, and do not fold it into any quoted flow range.

Inlet total pressure cannot be reported at all. The extracted table has only 9 negative-pressure values (339, 335, 330, 334, 332, 331, 365, 362, 359 Pa) for 4 conditions x 3 coal grades = 12 expected cells — the row-to-condition mapping is not recoverable from this extract. I'm not guessing which triplet belongs to which condition.

Both issues require reading the original .doc (not the pre-extracted text) to resolve — the extraction has visibly merged/misaligned table cells.

The defensible flow range for the corpus is 239.4–351.0 m³/s (TMCR-worst to TB-best) and the defensible pressure-rise range is 4,059–5,730 Pa — these three conditions (TB, 100% BMCR, TMCR) are internally consistent and monotonic; only 60% BMCR is unusable.

This is specification data only — no measured Unit-5 FD fan flow or pressure-rise data exists in this corpus to compare against these design figures (there's no per-fan flow instrumentation, and FD data never overlaps with a load/MW signal). Any "deviation from design" claim would be unsupportable, as covered earlier.

Bearing design limits referenced elsewhere in this spec (§4.3.8): rolling bearing (SKF/FAG), normal ≤70°C, max ≤80°C — separate from the flow/pressure duty table above.

Would you like me to pull the OEM performance-curve description (§4.2.3–4.2.5, e.g., stall-line and parallel-operation requirements) or the motor duty data sheet next?

stop_reason: end_turn | tokens: {'input_tokens': 149442, 'output_tokens': 2428, 'cache_read_tokens': 48077, 'cache_creation_tokens': 0, 'total_tokens': 151870, 'model_call_count': 2}

# Q4.  What are the Auxiliary power consumptions of FD Fan B at different loads?

Asked: 2026-08-11T09:50:25.777114+00:00

ForgeAI Response

TOOL CALL 1: Forgeai Get Source Datasets [OK, 409 ms] Getting datasets for ForgeAI source 665 source_id: 665 search_word: fdfan1 Result preview: Dataset ID; Dataset Name; Schema Name; Dataset Type ID; Dataset Type; Dataset Path; Row Count Estimate; Data Volume Bytes; .... 3402218; chart2_fdfan1; fd_fan_data; 1; TABLE; 1434; .... 3402219; chart1_fdfan1; fd_fan_data; 1; TABLE; 4299; .... 3402217; chart3_fdfan1; fd_fan_data; 1; TABLE; 1434; .... Showing 3 of 3 row(s) returned. (Total Datasets: 3 ¦ Page: 1 ¦ Page Size: 10 ¦ Total Pages: 1)

TOOL CALL 2: Github Get Repository [OK, 1415 ms] Getting repository details for sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant Result preview: Property; Value. Repository; sandhyatenneti/poc-power-plant. Description. Language. Stars; 0. Forks; 0. Watchers; 0. Showing 6 of 95 row(s) returned.

TOOL CALL 3: Github Get Content [OK, 839 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/PROFILE_REPORT.md Result preview: File: PROFILE_REPORT.md in sandhyatenneti/poc-power-plant Size: 7720 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/PROFILE_REPORT.md Content: ``` # PowerPlay Data Profile _Generated 2026-07-15 10:15 by `profile/profile_powerplay.py`._ Condition-monitoring corpus for the boiler draft fans (FD / PA / ID, each an A/B pair) of **Adani Tiroda Thermal Power Station, Unit 5**. This profile maps every entity and attribute in the corpus and gives a full statistical profile of the telemetry. ## Scale - **2,430,472** telemetry observations across **12** CSV files, melted to **250** canonical signals - **6** fans, **53** components, **14** metrics, **36** FMEA edg [Truncated — 7,856 characters total]

TOOL CALL 4: Github Get Content [OK, 1789 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/extracted/Tech-Specs__FD_fan_technical_specification_Rev.A.txt Result preview: File: Tech-Specs__FD_fan_technical_specification_Rev.A.txt in sandhyatenneti/poc-power-plant Size: 107686 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/extracted/Tech-Specs__FD_fan_technical_specification_Rev.A.txt Content: ``` TIRODA THERMAL POWER PROJECT 1980 MW (2x660 MW Phase I + 1x660 MW Phase II) Tiroda, Gondia District, Maharashtra Forced Draft Fan Technical Specification REV.A Southwest Electric Power Design Institute September , 2009CONTENTS TOC \o "1-2" \h \z \u HYPERLINK \L "_TOC228282783" PART I Technical Specification PAGEREF _TOC228282783 \H 1 HYPERLINK \L "_TOC228282784" 1 General Condition PAGEREF _TOC228282784 \H 1 [Truncated — 107,173 characters total]

TOOL CALL 5: Forgeai Get Dataset Schema [OK, 353 ms] Getting schema for dataset 3402219 from source 665 source_id: 665 dataset_id: 3402219 Result preview: Column ID; Column Name; Column Type. 14471; id; integer. 14472; row_seq; integer. 14473; reading_time_raw; string. 14474; reading_time; timestamp. 14475; furnace_lf_sd_olt_sa_flow; double. 14476; furnace_rt_sd_olt_sa_flow; double. Showing 6 of 73 row(s) returned.

TOOL CALL 6: Forgeai Get Dataset Column Profiles [OK, 587 ms] source_id: 665 dataset_id: 3402219 column_name: fdf_b_motor_current Result preview: Dataset Row Count: 4299 Dataset Column Count: 1 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count fdf_b_motor_current¦double¦Electrical current drawn by Fan B's motor, indicating operational load and potential electrical issues.¦AI Generated¦1015¦0¦4299¦No¦47.6777344¦58.5703125¦53.04¦¦¦¦48.40039 (21), 48.081543 (20), 48.06201 (20), 48.0556641 (19), 48.06836 (18)¦52.5869141 (1), 58.3881836 (1), 52.8085938 (1), 56.2006836 (1), 50.9917 (1)¦¦0 UNIQUE KEY DETAILS (Total: 4): KEY: id (primary [Truncated — 1,585 characters total]

TOOL CALL 7: Github Get Content [OK, 1144 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/extracted/Manuals__Instruction_Manual_For_FD_Fan.txt Result preview: File: Manuals__Instruction_Manual_For_FD_Fan.txt in sandhyatenneti/poc-power-plant Size: 99860 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/extracted/Manuals__Instruction_Manual_For_FD_Fan.txt Content: ``` ﻿ COMPONENT MANUAL FOR FORCED DRAUGHT FANS (FD-FANS) Facility: FD-Fan (600+600+600 MW unit) Power plant: EREN TURKEY Fan type: FAF26.6-15-1 Machine No. : Year of construction: 2010 SBW Project No.: 2010-034 This instruction is exclusive property of SBW. Availability is limited to supervisors or service personnel. Surrender to or access by third persons, as well as duplication of the plant in its entirety or in parts is prohibited. We rese [Truncated — 99,788 characters total]

TOOL CALL 8: Forgeai Get Dataset Column Profiles [OK, 494 ms] source_id: 665 dataset_id: 3402219 column_name: total_secondary_air_flow Result preview: Dataset Row Count: 4299 Dataset Column Count: 1 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count total_secondary_air_flow¦double¦Total secondary air flow delivered to the furnace, critical for combustion control and energy management.¦AI Generated¦3828¦0¦4299¦No¦1016.03906¦1637.03125¦1302.32¦¦¦¦1519.92188 (5), 1506.98438 (4), 1185.92188 (4), 1174.46875 (3), 1079.65625 (3)¦1520.65625 (1), 1506.73438 (1), 1538.17188 (1), 1330.5 (1), 1537.875 (1)¦¦0 UNIQUE KEY DETAILS (Total: 4): KEY: id ( [Truncated — 1,593 characters total]

TOOL CALL 9: Forgeai Execute [OK, 445 ms] source_id: 665 query: WITH bands AS ( SELECT fdf_b_motor_current, total_secondary_air_flow, fdf_b_inlet_vane_position, CASE WHEN total_secondary_air_flow < 1016.03906 + (1637.03125-1016.03906)/3.0 THEN '1_Low' WH … query_timeout_seconds: 30 Result preview: band:25; n:20; avg_current:1700; min_current:1700; max_current:1700; avg_flow:1700; avg_vane:1700. 1_Low; 1666; 48.6; 47.7; 53.3; 1111.5; 26.4. 2_Mid; 1326; 56.2; 48.0; 58.6; 1331.9; 40.9. 3_High; 1307; 55.5; 51.0; 57.1; 1515.6; 40.3. 3 rows. Showing 4 of 4 row(s) returned.

TOOL CALL 10: Forgeai Execute [OK, 660 ms] source_id: 665 query: SELECT round(corr(fdf_b_motor_current, total_secondary_air_flow)::numeric,3) AS corr_current_flow, round(corr(fdf_b_motor_current, fdf_b_inlet_vane_position)::numeric,3) AS corr_current_vane, round(avg(fdf_b_motor_ … query_timeout_seconds: 30 Result preview: corr_current_flow:1700; corr_current_vane:1700; overall_avg_current:1700; overall_min_current:1700; overall_max_current:1700. 0.801; 0.989; 53.0; 47.7; 58.6. 1 row. Showing 2 of 2 row(s) returned.

### FD Fan B "Auxiliary Power Consumption" at Different Loads

The corpus cannot answer this in kW. Per the corpus itself: *"No kW, voltage, power factor, or per-fan flow anywhere. Current is the only electrical measurement."* FD Fan B's motor data sheet in the OEM technical spec (§8.3) has a rated-current field, but it was left blank in the extracted document — so there is no rated current to convert amps to kW, and no voltage/power-factor reading exists anywhere in the telemetry to do the calculation directly. The closest defensible answer is motor current (A) by load band, with load itself approximated by a proxy (FD has no MW signal — see below).

Source: Power_Plant (source_id 665), table fd_fan_data.chart1_fdfan1, 4,299 rows, 23–26 Dec 2018. Load proxy: `total_secondary_air_flow` (plant-level secondary air flow, TPH) since FD data never overlaps with the ID tables' MW readings.

One-sentence answer: FD Fan B's motor current averages 48.6 A at the lowest flow band and climbs to about 55.5–56.2 A at mid-to-high flow, a rise of roughly 7 A (about 15%) as load increases — current tracks inlet vane position almost perfectly (correlation 0.99, very strong) and tracks flow strongly (correlation 0.80).

#### Table — Average current by flow band (load proxy)

| Band | Rows | Avg current (A) | Min current (A) | Max current (A) | Avg flow (TPH) | Avg vane position (%) |
| --- | --- | --- | --- | --- | --- | --- |
| Low | 1,666 | 48.6 | 47.7 | 53.3 | 1,111.5 | 26.4 |
| Mid | 1,326 | 56.2 | 48.0 | 58.6 | 1,331.9 | 40.9 |
| High | 1,307 | 55.5 | 51.0 | 57.1 | 1,515.6 | 40.3 |

Overall window: average current 53.0 A, range 47.7–58.6 A.

#### Caveats

This is current (A), not power (kW). Current is single-phase and CT-scaled per the corpus rules, so it corroborates loading trends but is not an absolute power/energy figure. No rated current, voltage, or power factor value is available anywhere in this corpus to convert it — the motor data sheet field for rated current is blank in the extracted spec, and telemetry carries no voltage/PF channel.

No MW/load signal exists for FD. FD data is December 2018 only; MW only exists in the ID tables (April/June/July), which never overlap with FD. total_secondary_air_flow is used here as the load proxy, as instructed — this is stated explicitly rather than silently substituted.

Current does not rise monotonically — it's actually slightly higher in the Mid band (56.2 A) than the High band (55.5 A), a roughly 0.7 A difference that is a modest, not dramatic, discrepancy — flow and vane position both still rise from Mid to High. This is a shape worth noting, not a data error.

Every count above comes from a count(*) run in this turn (1,666 / 1,326 / 1,307 rows, totalling the table's 4,299 rows).

This is a 3-day historian chart export, a screening sample, not a continuous trend or degradation record.

#### Chart

What would be needed for a true kW figure: the motor's rated current/voltage/power factor from the OEM data sheet (currently blank in the extract — would require the original .doc) plus a direct kW or power-factor telemetry channel, neither of which exists in this corpus.

stop_reason: end_turn | tokens: {'input_tokens': 754849, 'output_tokens': 9050, 'cache_read_tokens': 289596, 'cache_creation_tokens': 0, 'total_tokens': 763899, 'model_call_count': 7}

# Q5.  What are the applicable alarm and trip limits of ID Fan? give the response by executing the tools and git

Asked: 2026-08-11T09:59:35.259917+00:00

ForgeAI Response

TOOL CALL 1: Github Get Content [OK, 1102 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/extracted/Manuals__ID_Fan_O_M_Manual.txt Result preview: File: Manuals__ID_Fan_O_M_Manual.txt in sandhyatenneti/poc-power-plant Size: 88683 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/extracted/Manuals__ID_Fan_O_M_Manual.txt Content: ``` SHANGHAI BLOWER WORKS CO., LTD. Phone: 086/021-56650577 Fax: 086/021-56651514 E-mail: design@sbw-cn.com COMPONENT MANUAL FOR INDUCED DRAUGHT FANS (ID-FANS) Facility: ID-Fan (2x660 MW unit) Power plant: FGD TIRODA Fan type: SAF36.5-19-2 Machine No. : Year of con [Truncated — 88,700 characters total]

TOOL CALL 2: Github Get Content [OK, 1210 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/extracted/Tech-Specs__ID_fan_technical_specification_Rev.A.txt Result preview: File: Tech-Specs__ID_fan_technical_specification_Rev.A.txt in sandhyatenneti/poc-power-plant Size: 110167 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/extracted/Tech-Specs__ID_fan_technical_specification_Rev.A.txt Content: ``` TIRODA THERMAL POWER PROJECT 1980 MW (2x660 MW Phase I + 1x660 MW Phase II) Tiroda, Gondia District, Maharashtra Induced Draft Fan Technical Specification REV.A Southwest Electric Power Design Institute September, 2009 CONTENTS TOC \o "1-2" \h \z \u HYPERLINK \L "_TOC228332399" PART I Technical Specification PAGEREF _TOC228332399 \H 1 HYPERLINK \L "_TOC228332400" 1 General Condition PAGEREF _TOC228332400 \H 1 [Truncated — 109,639 characters total]

### ID Fan Alarm and Trip Limits — Adani Tiroda Unit 5

One-sentence answer: The ID fan (Shanghai Blower Works, model SAF36.5-19-2) uses the same supervision table cited for all three OEM manuals — bearing temperature alarm at 90°C and trip at 120°C, vibration alarm at 4.5 mm/s and trip at 11 mm/s — with a separate, lower design limit of 70°C normal / 80°C max for the rolling bearing element itself.

Sources: Manuals__ID_Fan_O_M_Manual.txt (Shanghai Blower Works COMPONENT MANUAL, §5.3.2 "Fan start permissive" and §5.3.3 "Supervision of operation"); Tech-Specs__ID_fan_technical_specification_Rev.A.txt (§4.3.9).

#### Table 1 — Alarm and trip set points (O&M Manual, §5.3.3, table applies identically across FD/PA/ID per the manuals)

| Condition | Threshold | Action |
| --- | --- | --- |
| Main bearing temperature | > 90°C | Alarm — check oil cooling |
| Main bearing temperature | > 120°C | Trip fan — leave oil running for 10 min |
| Fan vibration | > 4.5 mm/s | Alarm — analyze problem |
| Fan vibration | > 11 mm/s | Trip fan |
| Fan operating in stall | — | Alarm — reduce fan output by reducing blade pitch (closing blades) |

#### Table 2 — Fan start permissive conditions (O&M Manual, §5.3.2) and other operational set points

| Condition | Threshold / requirement |
| --- | --- |
| Lube oil flow | > 3 L/min required for start; also alarm condition if seen during operation |
| Oil pressure | > 2.5 MPa required for start; low pressure during operation -> alarm, start auxiliary pump |
| Main bearing temperature (pre-start) | < 90°C required for start |
| Blades | Must be closed before start |
| Oil reservoir temperature | < 30°C -> heaters on; > 40°C -> heaters off |

#### Design (not alarm/trip) bearing limit — separate reference

Per the ID fan technical specification, §4.3.9: the main bearing is an imported rolling bearing (SKF or FAG), with normal working temperature not higher than 70°C and maximum temperature not to exceed 80°C. This is a design/manufacturing limit distinct from the 90°C/120°C alarm/trip set points above — the spec explicitly states "the bidder shall provide the alarm value and trip value of bearing temperature" separately, confirming the O&M manual's 90/120°C figures are the actual field set points, while 70/80°C is the bearing manufacturer's design ceiling.

#### Caveats

These alarm/trip values come from the same supervision table repeated in all three OEM manuals (FD, PA, ID) — I am citing the ID fan's own manual copy, per the corpus convention of citing the manual for the fan being discussed.

The metadata tag dictionary's Alarm/Trip/Engineering-limit columns are empty in this corpus — these values are sourced directly from the O&M manual document text, not from any dataset field.

No measured ID fan bearing temperature or vibration reading has been checked against these limits in this turn — this response is document-only, as requested ("by executing the tools and git[Hub]"). If you want the actual measured max/p95 values compared against these thresholds (per the corpus's "Limit screening" method), I can run that as a follow-up query against the ID fan tables (April/June/July 2018 windows).

Design duty performance guarantee fields (§5.3, e.g., "Fan bearing temperature rise," "Fan bearing vibration speed root-mean-square value") were left as blank fill-in fields in the specification template — no numeric guarantee values are available for those, separate from the alarm/trip table above.

Would you like me to now query the ID-A/ID-B tables for max and p95 bearing temperature and vibration values against these limits, split by load window (April full-load, July ~60% load, June unit-down)?

stop_reason: end_turn | tokens: {'input_tokens': 183597, 'output_tokens': 1963, 'cache_read_tokens': 48077, 'cache_creation_tokens': 0, 'total_tokens': 185560, 'model_call_count': 2}

# Q6.  For how long ID Fan A operated at full load?

Asked: 2026-08-11T10:06:18.026019+00:00

ForgeAI Response

TOOL CALL 1: Forgeai Get Source Datasets [OK, 347 ms] Getting datasets for ForgeAI source 665 source_id: 665 search_word: idfan_a Result preview: Dataset ID; Dataset Name; Schema Name; Dataset Type ID; Dataset Type; Dataset Path; Row Count Estimate; Data Volume Bytes; .... 3402222; chart3_idfan_a; id_fan_data; 1; TABLE; 1423; .... 3402221; chart2_idfan_a; id_fan_data; 1; TABLE; 5728; .... 3402220; chart1_idfan_a; id_fan_data; 1; TABLE; 4157; .... Showing 3 of 3 row(s) returned. (Total Datasets: 3 ¦ Page: 1 ¦ Page Size: 10 ¦ Total Pages: 1)

TOOL CALL 2: Forgeai Get Dataset Schema [OK, 304 ms] Getting schema for dataset 3402221 from source 665 source_id: 665 dataset_id: 3402221 Result preview: Column ID; Column Name; Column Type. 14705; Column1; integer. 14707; Unnamed: 0; integer. 14709; Boiler SystemTOTAL AIR FLOW; double. 14711; Boiler SystemTOTAL COAL FLOW; double. 14714; ID Fan A Bearing 1IDF A #1 BEARING TEM; double. 14716; ID Fan A Bearing 1IDF A #1 BEARING TEM.1; float. Showing 6 of 47 row(s) returned.

TOOL CALL 3: Forgeai Get Dataset Column Profiles [OK, 598 ms] source_id: 665 dataset_id: 3402221 column_name: MEGAWATT Result preview: Dataset Row Count: 5728 Dataset Column Count: 1 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count Tiroda Unit 5MEGAWATT¦double¦Gross megawatt output for Tiroda Unit 5, likely redundant with 'Actual Turbine Gross Output'.¦AI Generated¦2722¦0¦5728¦No¦443.79296875¦660.6171875¦518.96¦¦¦¦470.140625 (242), 648.75 (9), 470.34375 (9), 652.15625 (9), 471.92578125 (9)¦444.890625 (1), 448.61328125 (1), 536.296875 (1), 645.2890625 (1), 537.171875 (1)¦¦0 UNIQUE KEY DETAILS (Total: 3): KEY: Column1 (P [Truncated — 1,366 characters total]

TOOL CALL 4: Forgeai Get Dataset Column Profiles [OK, 813 ms] source_id: 665 dataset_id: 3402221 column_name: Time Result preview: Dataset Row Count: 5728 Dataset Column Count: 1 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count Time¦string¦Timestamp of each reading, providing the temporal context for all operational data in the table.¦AI Generated¦5728¦0¦5728¦No¦4/10/18 10:00 AM¦4/9/18 9:59 PM¦¦14.62¦14¦16¦4/7/18 1:48 PM (1), 4/7/18 2:24 PM (1), 4/7/18 8:24 PM (1), 4/7/18 10:48 PM (1), 4/8/18 9:18 AM (1)¦4/7/18 1:48 PM (1), 4/7/18 2:24 PM (1), 4/7/18 8:24 PM (1), 4/7/18 10:48 PM (1), 4/8/18 9:18 AM (1)¦¦0 UNIQUE KEY [Truncated — 1,403 characters total]

TOOL CALL 5: Forgeai Execute [OK, 355 ms] source_id: 665 query: SELECT count(*) FILTER (WHERE "Tiroda Unit 5MEGAWATT" >= 627) AS cnt_full_627, count(*) FILTER (WHERE "Tiroda Unit 5MEGAWATT" >= 640) AS cnt_full_640, count(*) AS total_cnt, min("Tiroda Unit 5MEGAWATT") AS min_mw … Result preview: cnt_full_627:20; cnt_full_640:20; total_cnt:20; min_mw:700; max_mw:700; avg_mw:701. 1292; 1282; 5728; 443.79297; 660.6172; 518.9550024277671. 1 row. Showing 2 of 2 row(s) returned.

### Duration ID Fan A Operated at Full Load

One-sentence answer: ID Fan A operated at full/base load (≥627 MW) for approximately 21 hours 32 minutes out of the April window, or a slightly stricter 21 hours 22 minutes at a ≥640 MW cutoff — a large majority of the recorded period, since this window (7–11 April 2018) is specifically the plant's full-load screening sample.

Source: Power_Plant (source_id 665), table id_fan_data.chart2_idfan_a, 5,728 rows, 7–11 Apr 2018 — this is the ID-A table that the corpus pairs with the April/full-load window (paired with chart3_idfan_b for the same window). MW column used: Tiroda Unit 5MEGAWATT (= ACTUAL TURBINE GROSS OUTPUT), rated 660 MW.

#### Table — Duration at full load, two thresholds

| Threshold | Rows meeting threshold | Duration (rows x 60s) | Duration (h:m) | % of table window |
| --- | --- | --- | --- | --- |
| ≥ 627 MW (corpus full/base-load definition) | 1,292 | 77,520 s | 21h 32m | 22.6% |
| ≥ 640 MW (stricter cutoff) | 1,282 | 76,920 s | 21h 22m | 22.4% |

Table-wide MW stats (all 5,728 rows): min 443.8 MW, max 660.6 MW, average 519.0 MW — confirming the window spans well below to right at rated output, not a constant full-load run.

#### Caveats

Every count above comes from a count(*) run in this turn — 1,292 rows at ≥627 MW and 1,282 rows at ≥640 MW, out of the table's full 5,728 rows.

Duration is computed as distinct-timestamp count x 60 s cadence, per the corpus method — this assumes no gaps in the 60 s sampling, which hasn't been separately verified row-by-row in this turn.

This is a hand-picked historian chart export (7–11 Apr 2018), not a continuous feed — it's a ~4-day screening sample, not a full operating history, so this duration describes only what's captured in this export, not the unit's total full-load runtime.

MW exists only in the ID tables in this corpus; this figure cannot be cross-checked against FD or PA data (no overlap, no MW there).

Max observed (660.6 MW) is essentially at rated capacity (660 MW) — no impossible/out-of-range values were found, so no values were rejected here.

Would you like the same duration breakdown for ID Fan B's corresponding April window (chart3_idfan_b), or a bearing-temperature/vibration check specifically during these full-load hours?

stop_reason: end_turn | tokens: {'input_tokens': 318856, 'output_tokens': 2933, 'cache_read_tokens': 192388, 'cache_creation_tokens': 0, 'total_tokens': 321789, 'model_call_count': 5}

# Q7.  Which ID Fan did consume more power at same load?

Asked: 2026-08-11T10:08:01.708640+00:00

ForgeAI Response

TOOL CALL 1: Forgeai Get Source Datasets [OK, 337 ms] Getting datasets for ForgeAI source 665 source_id: 665 search_word: idfan Result preview: Dataset ID; Dataset Name; Schema Name; Dataset Type ID; Dataset Type; Dataset Path; Row Count Estimate; Data Volume Bytes; .... 3402225; chart1_idfan_b; id_fan_data; 1; TABLE; 1423; .... 3402224; chart3_idfan_b; id_fan_data; 1; TABLE; 5728; .... 3402223; chart2_idfan_b; id_fan_data; 1; TABLE; 4157; .... 3402222; chart3_idfan_a; id_fan_data; 1; TABLE; 1423; .... 3402221; chart2_idfan_a; id_fan_data; 1; TABLE; 5728; .... 3402220; chart1_idfan_a; id_fan_data; 1; TABLE; 4157; .... Showing 6 of 6 row(s) returned. (Total Datasets: 6 ¦ Page: 1 ¦ Page Size: 10 ¦ Total Pages: 1)

TOOL CALL 2: Forgeai Get Dataset Schema [OK, 385 ms] Getting schema for dataset 3402221 from source 665 source_id: 665 dataset_id: 3402221 Result preview: Column ID; Column Name; Column Type. 14705; Column1; integer. 14707; Unnamed: 0; integer. 14709; Boiler SystemTOTAL AIR FLOW; double. 14711; Boiler SystemTOTAL COAL FLOW; double. 14714; ID Fan A Bearing 1IDF A #1 BEARING TEM; double. 14716; ID Fan A Bearing 1IDF A #1 BEARING TEM.1; float. Showing 6 of 47 row(s) returned.

TOOL CALL 3: Forgeai Get Dataset Schema [OK, 588 ms] Getting schema for dataset 3402224 from source 665 source_id: 665 dataset_id: 3402224 Result preview: Column ID; Column Name; Column Type. 14774; Column1; integer. 14775; Unnamed: 0; integer. 14776; Boiler SystemTOTAL AIR FLOW; double. 14777; Boiler SystemTOTAL COAL FLOW; double. 14778; ID Fan B Bearing 1IDF B #1 BEARING TEMP; double. 14779; ID Fan B Bearing 1IDF B #1 BEARING TEMP.1; float. Showing 6 of 48 row(s) returned.

TOOL CALL 4: Forgeai Execute [OK, 636 ms] source_id: 665 query: WITH filtered AS ( SELECT "Tiroda Unit 5MEGAWATT" AS mw, "ID Fan BIDF B CURRENT FOR SINGLE PHASE" AS cur FROM id_fan_data.chart1_idfan_b WHERE "Tiroda Unit 5MEGAWATT" > 0 AND "ID Fan BIDF B CURRENT FOR SINGLE PHASE … Result preview: ERROR[EXECUTION_ERROR]: column "Tiroda Unit 5MEGAWATT" does not exist LINE 1: WITH filtered AS (SELECT "Tiroda Unit 5MEGAWATT" AS mw, "ID ... ^ query: WITH filtered AS ( SELECT "Tiroda Unit 5MEGAWATT" AS mw, "ID Fan BIDF B CURRENT FOR SINGLE PHASE" AS cur FROM id_fan_data.chart1_idfan_b WHERE "Tiroda Unit 5MEGAWATT" > 0 AND "ID Fan BIDF B CURRENT FOR SINGLE PHASE" > 0 ), bucketed AS ( SELECT mw, cur, ntile(4) OVER (ORDER BY mw) AS bucket FROM filtered ) SELECT bucket, count(*) AS n, avg(mw) AS avg_mw, min(mw) AS min_mw, max(mw) AS max_mw, avg(cur) AS avg_current FROM bucketed GROUP BY bucket ORDER BY bucket

TOOL CALL 5: Forgeai Execute [OK, 756 ms] source_id: 665 query: WITH filtered AS ( SELECT "Tiroda Unit 5MEGAWATT" AS mw, "ID Fan BIDF B CURRENT FOR SINGLE PHASE" AS cur FROM id_fan_data.chart3_idfan_b WHERE "Tiroda Unit 5MEGAWATT" > 0 AND "ID Fan BIDF B CURRENT FOR SINGLE PHASE … Result preview: bucket:23; n:20; avg_mw:701; min_mw:700; max_mw:700; avg_current:701. 1; 1432; 458.0856401667249; 443.79297; 465.8047; 104.98141530638966. 2; 1432; 469.84083395164106; 465.82422; 472.72656; 106.51695822603875. 3; 1432; 506.9395649659567; 472.72656; 537.1719; 112.73400606123428. 4; 1432; 640.9539706267458; 537.22656; 660.6172; 156.63063364721543. 4 rows. Showing 5 of 5 row(s) returned.

TOOL CALL 6: Forgeai Execute [OK, 1233 ms] source_id: 665 query: WITH filtered AS ( SELECT "Tiroda Unit 5MEGAWATT" AS mw, "ID Fan AIDF A CURRENT FOR SINGLE PHASE" AS cur FROM id_fan_data.chart3_idfan_a WHERE "Tiroda Unit 5MEGAWATT" > 0 AND "ID Fan AIDF A CURRENT FOR SINGLE PHASE … Result preview: bucket:23; n:20; avg_mw:701; min_mw:700; max_mw:700; avg_current:701. 1; 356; 384.4288426088483; 377.52344; 388.10938; 100.34627918714888. 2; 356; 390.4997586025281; 388.16406; 392.66797; 99.94174640098315. 3; 356; 395.7889856917135; 392.66797; 398.91797; 100.4659547270014. 4; 355; 403.2135563380282; 398.9375; 423.7578; 101.1402041153169. 4 rows. Showing 5 of 5 row(s) returned.

TOOL CALL 7: Forgeai Execute [OK, 1233 ms] source_id: 665 query: WITH filtered AS ( SELECT "Tiroda Unit 5MEGAWATT" AS mw, "ID Fan AIDF A CURRENT FOR SINGLE PHASE" AS cur FROM id_fan_data.chart2_idfan_a WHERE "Tiroda Unit 5MEGAWATT" > 0 AND "ID Fan AIDF A CURRENT FOR SINGLE PHASE … Result preview: bucket:23; n:20; avg_mw:701; min_mw:700; max_mw:700; avg_current:701. 1; 1432; 458.0856401667249; 443.79297; 465.8047; 103.52093198978702. 2; 1432; 469.84083395164106; 465.82422; 472.72656; 104.74450819985161. 3; 1432; 506.9395649659567; 472.72656; 537.1719; 110.14658394072976. 4; 1432; 640.9539706267458; 537.22656; 660.6172; 143.13398273830308. 4 rows. Showing 5 of 5 row(s) returned.

TOOL CALL 8: Forgeai Get Dataset Schema [OK, 316 ms] Getting schema for dataset 3402225 from source 665 source_id: 665 dataset_id: 3402225 Result preview: Column ID; Column Name; Column Type. 14880; id; integer. 14883; row_id; integer. 14885; row_seq; integer. 14888; total_air_flow; double. 14891; total_coal_flow; double. 14894; furnace_pressure; double. Showing 6 of 51 row(s) returned.

TOOL CALL 9: Forgeai Execute [OK, 328 ms] source_id: 665 query: WITH filtered AS ( SELECT megawatt AS mw, idf_b_motor_current AS cur FROM id_fan_data.chart1_idfan_b WHERE megawatt > 0 AND idf_b_motor_current > 0 ), bucketed AS ( SELECT mw, cur, ntile(4) OVER (ORDER BY mw) AS … Result preview: bucket:23; n:20; avg_mw:701; min_mw:701; max_mw:701; avg_current:701. 1; 356; 384.4288431123595; 377.523438; 388.109375; 100.14239129803379. 2; 356; 390.4997586769662; 388.164063; 392.667969; 101.00943348005626. 3; 356; 395.78898567415735; 392.667969; 398.917969; 102.21024612893267. 4; 355; 403.21355677183124; 398.9375; 423.7578; 103.63692502535226. 4 rows. Showing 5 of 5 row(s) returned.

### Which ID Fan Consumed More Power at the Same Load

Important scope note first: The corpus has no kW measurement anywhere — motor current (single-phase, CT-scaled) is the only electrical signal available, and per the corpus, absolute current is not directly comparable between two different machines (different CT scaling). So this compares current at matched MW, corroborating a duty-split signal, not verified "power consumption."

Sources, matched by the corpus's stated ID-A/ID-B pairing rule (chart numbers don't align between A and B):

April (full/base load, 443–660 MW): id_fan_data.chart2_idfan_a (ID-A) paired with id_fan_data.chart3_idfan_b (ID-B), 5,728 rows each, 7–11 Apr 2018

July (~60% load, 377–424 MW): id_fan_data.chart3_idfan_a (ID-A) paired with id_fan_data.chart1_idfan_b (ID-B), 1,423/1,434 rows, 1 Jul 2018

One-sentence answer: At matched MW, ID Fan B draws more current than ID Fan A in both windows, but the gap is dramatic at full load (up to 156.6 A vs 143.1 A, a 13.5 A / ~9% difference at the highest bucket) and only marginal at ~60% load (0.2–2.5 A), so ID-B is the more heavily loaded fan electrically, especially as load rises toward rated capacity.

#### Table 1 — April window, full/base load (quartiles by MW, matched between tables)

| MW bucket | Avg MW (both tables) | ID-A avg current (A) | ID-B avg current (A) | B − A (A) |
| --- | --- | --- | --- | --- |
| 1 (lowest) | 458.1 | 103.5 | 105.0 | +1.5 |
| 2 | 469.8 | 104.7 | 106.5 | +1.8 |
| 3 | 506.9 | 110.1 | 112.7 | +2.6 |
| 4 (highest) | 641.0 | 143.1 | 156.6 | +13.5 |

#### Table 2 — July window, ~60% load (quartiles by MW, matched between tables)

| MW bucket | Avg MW (both tables) | ID-A avg current (A) | ID-B avg current (A) | B − A (A) |
| --- | --- | --- | --- | --- |
| 1 (lowest) | 384.4 | 100.3 | 100.1 | −0.2 |
| 2 | 390.5 | 99.9 | 101.0 | +1.1 |
| 3 | 395.8 | 100.5 | 102.2 | +1.8 |
| 4 (highest) | 403.2 | 101.1 | 103.6 | +2.5 |

#### Caveats

Sign checked: in every bucket except July's lowest, B − A is positive, meaning ID-B's current is larger than ID-A's — confirmed by re-reading both raw values before writing this, not inferred from the difference column alone.

Absolute current is not strictly comparable between two different machines (per corpus rule: current is single-phase and CT-scaled). The April full-load gap (13.5 A, ~9%) is large enough to be a real duty-split signal worth investigating with flow/vane position, but it should be corroborated, not taken alone, as proof ID-B "consumes more power."

No kW, voltage, or power factor exists anywhere in this corpus — this is a current comparison, not a verified power comparison. To get true power consumption, per-fan kW/PF instrumentation would be needed, which does not exist here.

The MW buckets are identical between the paired A/B tables (e.g. bucket 4 avg MW = 640.95 in both) — confirming the pairing (April: chart2_idfan_a <-> chart3_idfan_b) correctly aligns the same underlying unit-level MW readings, so this is a genuine matched-load comparison, not an artifact of mismatched windows.

These are two separate historian chart exports (April and July), each a multi-day screening sample, not a continuous trend.

Every count and average above comes from a count(*)/avg() run in this turn; the first output line in each query result was column-width metadata (ignored, not a data row).

#### Chart

Bottom line: ID Fan B runs at higher current than ID Fan A at every matched load point checked, with the gap widening sharply as load approaches rated capacity (April Q4). This is a corroborating electrical signal, not confirmed kW — if a firmer power-consumption conclusion is needed, I'd recommend also checking flow/vane-position duty split between the two fans (as the corpus method prescribes for fan comparisons) before treating this as a maintenance or efficiency finding.

stop_reason: end_turn | tokens: {'input_tokens': 406506, 'output_tokens': 10496, 'cache_read_tokens': 240485, 'cache_creation_tokens': 0, 'total_tokens': 417002, 'model_call_count': 6}

# Q8.  How many PA Fans are in operation at full load?

Asked: 2026-08-11T10:13:36.729151+00:00

ForgeAI Response

TOOL CALL 1: Forgeai Get Dataset Schema [OK, 300 ms] Getting schema for dataset 1 from source 665 source_id: 665 dataset_id: 1 Result preview: Error getting dataset schema: ForgeAI API error: {'error': 'Dataset schema not found'} (Status: 404)

TOOL CALL 2: Forgeai Get Source Datasets [OK, 367 ms] Getting datasets for ForgeAI source 665 source_id: 665 search_word: pafan1 Result preview: Dataset ID; Dataset Name; Schema Name; Dataset Type ID; Dataset Type; Dataset Path; Row Count Estimate; Data Volume Bytes; .... 3402216; chart3_pafan1; pa_fan_data; 1; TABLE; 2012; .... 3402214; chart2_pafan1; pa_fan_data; 1; TABLE; 2012; .... 3402215; chart1_pafan1; pa_fan_data; 1; TABLE; 2014; .... Showing 3 of 3 row(s) returned. (Total Datasets: 3 ¦ Page: 1 ¦ Page Size: 10 ¦ Total Pages: 1)

TOOL CALL 3: Forgeai Get Dataset Schema [OK, 304 ms] Getting schema for dataset 3402215 from source 665 source_id: 665 dataset_id: 3402215 Result preview: Column ID; Column Name; Column Type. 14965; id; integer. 14966; row_seq; integer. 14967; reading_time_raw; string. 14968; reading_time; timestamp. 14969; idf_a_outlet_gas_pressure; double. 14970; idf_b_outlet_gas_pressure; double. Showing 6 of 172 row(s) returned.

TOOL CALL 4: Forgeai Get Dataset Column Profiles [OK, 925 ms] source_id: 665 dataset_id: 3402215 column_name: paf_a_motor_current Result preview: Dataset Row Count: 2014 Dataset Column Count: 1 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count paf_a_motor_current¦double¦Motor current for PAF A, indicating electrical load and motor performance.¦AI Generated¦1113¦0¦2014¦No¦73.79297¦106.728516¦82.37¦¦¦¦77.4082 (8), 76.70508 (8), 76.10742 (7), 76.0722656 (7), 76.34766 (7)¦78.73828 (1), 101.53125 (1), 88.95703 (1), 75.82031 (1), 79.6875 (1)¦¦0 UNIQUE KEY DETAILS (Total: 4): KEY: id (Primary Key) Method: PROFILED ¦ Confidence: 1.0 C [Truncated — 1,813 characters total]

TOOL CALL 5: Forgeai Get Dataset Column Profiles [OK, 1125 ms] source_id: 665 dataset_id: 3402215 column_name: total_coal_flow Result preview: Dataset Row Count: 2014 Dataset Column Count: 1 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count total_coal_flow¦double¦Total coal flow to the boiler, a fundamental variable for combustion control and efficiency analysis.¦AI Generated¦1836¦0¦2014¦No¦302.609375¦425.8086¦348.54¦¦¦¦314.339844 (4), 317.9297 (3), 315.925781 (3), 316.042969 (3), 311.0703 (3)¦323.78125 (1), 309.394531 (1), 315.417969 (1), 335.6211 (1), 314.90625 (1)¦¦0 UNIQUE KEY DETAILS (Total: 4): KEY: id (Primary Key) Met [Truncated — 1,848 characters total]

TOOL CALL 6: Forgeai Execute [OK, 357 ms] source_id: 665 query: WITH ranked AS ( SELECT total_coal_flow, paf_a_motor_current, paf_b_motor_current, ntile(4) OVER (ORDER BY total_coal_flow) AS band FROM pa_fan_data.chart1_pafan1 ) SELECT band, count(*) AS rows_in_ba … Result preview: band:23; rows_in_band:20; avg_coal_flow:1700; avg_current_a:1700; min_current_a:1700; avg_current_b:1700; min_current_b:1700. 1; 504; 309.4; 77.6; 74.0; 81.8; 80.7. 2; 504; 316.5; 77.8; 74.0; 82.5; 81.1. 3; 503; 353.2; 83.4; 73.8; 86.8; 81.6. 4; 503; 415.2; 90.7; 86.7; 92.6; 89.7. 4 rows. Showing 5 of 5 row(s) returned.

TOOL CALL 7: Forgeai Execute [OK, 369 ms] source_id: 665 query: WITH ranked AS ( SELECT total_coal_flow, paf_a_motor_current, paf_b_motor_current, ntile(4) OVER (ORDER BY total_coal_flow) AS band FROM pa_fan_data.chart1_pafan1 ), top_band AS ( SELECT * FROM ranked WHER … Result preview: total_rows_top_band:20; a_running_rows:20; b_running_rows:20; both_running_rows:20; both_off_rows:20; min_a:701; max_a:701; min_b:701; .... 503; 503; 503; 503; 0; 86.68945; 106.728516; 89.65234; .... 1 row; .... Showing 2 of 2 row(s) returned.

TOOL CALL 8: Forgeai Execute [OK, 327 ms] source_id: 665 query: SELECT count(*) AS total_rows, min(paf_a_motor_current) AS min_a, max(paf_a_motor_current) AS max_a, min(paf_b_motor_current) AS min_b, max(paf_b_motor_current) AS max_b, sum(CASE WHEN paf_a_motor_current <= 10 T … Result preview: total_rows:20; min_a:701; max_a:701; min_b:701; max_b:701; a_off_rows:20; b_off_rows:20. 2014; 73.79297; 106.728516; 80.67578; 103.418945; 0; 0. 1 row. Showing 2 of 2 row(s) returned.

### PA Fans in Operation at Full Load

No MW/load signal exists for PA (per corpus: PA data is December 2018, MW only exists in the ID tables which never overlap with PA). Using the stated proxy for PA — `total_coal_flow` (TPH) — and checking motor current as the "in operation" test.

Source: Power_Plant (source_id 665), table pa_fan_data.chart1_pafan1, 2,014 rows, 29–30 Dec 2018.

#### One-sentence answer

Both PA fans (PA-A and PA-B) are in operation at full load — at the highest coal-flow band (proxy for full load, avg 415.2 TPH), PA-A's motor current ranges 86.7–106.7 A and PA-B's ranges 89.7–103.4 A, with zero rows below a running threshold (10 A) — i.e. neither fan shows an "off/idle" reading anywhere in the highest-load band, or anywhere in the table at all.

#### Table — Motor current by coal-flow band (proxy for load)

| Band | Rows | Avg coal flow (TPH) | PA-A avg current (A) | PA-A min current (A) | PA-B avg current (A) | PA-B min current (A) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 (lowest) | 504 | 309.4 | 77.6 | 74.0 | 81.8 | 80.7 |
| 2 | 504 | 316.5 | 77.8 | 74.0 | 82.5 | 81.1 |
| 3 | 503 | 353.2 | 83.4 | 73.8 | 86.8 | 81.6 |
| 4 (highest, proxy for full load) | 503 | 415.2 | 90.7 | 86.7 | 92.6 | 89.7 |

#### Verification — running vs. off check, highest-load band and whole table

| Check | Result |
| --- | --- |
| Rows in highest-load band with PA-A current > 10 A | 503 of 503 (100%) |
| Rows in highest-load band with PA-B current > 10 A | 503 of 503 (100%) |
| Rows in highest-load band with both fans running | 503 of 503 (100%) |
| Rows in highest-load band with both fans off | 0 of 503 |
| PA-A current range, whole table (2,014 rows) | 73.8–106.7 A, 0 rows ≤10 A |
| PA-B current range, whole table (2,014 rows) | 80.7–103.4 A, 0 rows ≤10 A |

#### Caveats

Every count above comes from a count(*) run in this turn (504/504/503/503 rows per band = 2,014 total; 503/503/503/0 in the running-check on the top band).

"In operation" is inferred from motor current exceeding a 10 A threshold (a non-physical-value-style cutoff, since idle/off fans would show near-zero current, per the corpus's dead-channel convention) — there is no separate breaker/status flag column in this table to confirm run state directly.

This table (chart1_pafan1) already carries the corpus's own PA duty-quality caveats: esp_current_ib repeats ~12x and fill_to_flume holds misplaced timestamped rows — neither column was used in this analysis, so they don't affect this result.

total_coal_flow is a plant-level proxy for load, not per-fan flow (no per-fan flow measurement exists anywhere in this corpus) — stated explicitly per corpus convention rather than presented as MW.

This is a 2-day historian chart export (29–30 Dec 2018), a screening sample, not a continuous operating record — it doesn't prove PA fans always run in pairs at full load system-wide, only that both were running throughout this particular window, including its highest-load rows.

#### Chart

Bottom line: Both PA fans (A and B) are running continuously throughout this window, including at the highest coal-flow band used as a proxy for full load — there is no evidence of single-fan PA operation in this corpus. This is based on current, not a direct run-status flag or MW, since neither exists for PA in this corpus.

stop_reason: end_turn | tokens: {'input_tokens': 549795, 'output_tokens': 6823, 'cache_read_tokens': 336679, 'cache_creation_tokens': 0, 'total_tokens': 556618, 'model_call_count': 8}

# Q9.  Show deviation of FD Fan performance from characteristics curve at full load.

Asked: 2026-08-11T10:17:30.862584+00:00

ForgeAI Response

I flagged this same limitation for base/60% load earlier, and it applies identically at full load — nothing has changed in the corpus since then.

Deviation from the characteristic curve at full load cannot be computed for the FD fan, for two independent reasons:

No load reference exists for FD at all. FD data is exclusively December 2018 (chart1_fdfan1, chart2_fdfan1, chart3_fdfan1 — the last a duplicate of chart2, never to be combined). MW only exists in the ID tables (April/June/July 2018). FD and PA "can never be joined to MW" per the corpus — there is no window where FD telemetry coincides with a load reading, so "full load" cannot be identified in the FD data at all, let alone used to select rows for a deviation calculation. The closest available proxy is total_secondary_air_flow (TPH, 1,016–1,637 range) or <fan>_inlet_vane_position (%) — neither is MW, and I won't substitute one silently.

No characteristic curve exists in this corpus for Unit 5's FD fan. The only characteristic-curve document referenced anywhere in this corpus is for the Nagarjuna plant — explicitly a class-level reference only, never a Unit-5 measurement. There is no curve to compute a deviation against.

Even the design duty table (the nearest thing to a "curve" reference) has unresolved errors at exactly the load points relevant here:

The 100% BMCR row (the nearest defensible "full load" design point) gives inlet flow 267.8–292.5 m³/s and total pressure rise 4,112–4,407 Pa across the three coal grades — this part of the table is internally consistent and usable as a design reference point.

But the inlet total pressure mapping is unresolved (9 values extracted for 4 conditions x 3 coal grades = 12 expected cells) — so even pairing a measured proxy pressure against the correct design pressure at full load isn't possible without reading the original .doc.

There is no per-fan flow measurement anywhere in this corpus (flows are plant-level only), and fan differential pressure (<fan>_dp_inlet_outlet) is not the same quantity as "total pressure rise" in the design duty table — so even the measured proxy signals I do have aren't the same physical quantity as the design curve inputs.

What I can give you instead, if useful:

The 100% BMCR design point in isolation (flow 267.8–292.5 m³/s, pressure rise 4,112–4,407 Pa, 50°C inlet air, density 1.018 kg/m³) as a standalone spec reference, not compared to any measurement.

FD Fan A/B's measured dp_inlet_outlet, total_secondary_air_flow, and inlet_vane_position behavior at the highest end of the December window (as a "highest observed duty" proxy for full load), described in absolute terms only — explicitly not a deviation-from-curve figure.

What would actually be needed: a Unit-5-specific FD characteristic curve (not the Nagarjuna one), an FD operating window with a genuine load/MW reference, and the original .doc to resolve the pressure-row mapping.

Would either of the two things I can offer be useful, or should I leave this as a documented gap?

stop_reason: end_turn | tokens: {'input_tokens': 66355, 'output_tokens': 1207, 'cache_read_tokens': 0, 'cache_creation_tokens': 0, 'total_tokens': 67562, 'model_call_count': 1}

# Q10.  Based on operation parameters, can you recommend maintenance procedure for any of the fans?

Asked: 2026-08-11T10:18:20.267086+00:00

ForgeAI Response

TOOL CALL 1: Github Get Content [OK, 1323 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/extracted/Manuals__Instruction_Manual_For_FD_Fan.txt Result preview: File: Manuals__Instruction_Manual_For_FD_Fan.txt in sandhyatenneti/poc-power-plant Size: 99860 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/extracted/Manuals__Instruction_Manual_For_FD_Fan.txt Content: ``` ﻿ COMPONENT MANUAL FOR FORCED DRAUGHT FANS (FD-FANS) Facility: FD-Fan (600+600+600 MW unit) Power plant: EREN TURKEY Fan type: FAF26.6-15-1 Machine No. : Year of construction: 2010 SBW Project No.: 2010-034 This instruction is exclusive property of SBW. Availability is limited to supervisors or service personnel. Surrender to or access by third persons, as well as duplication of the plant in its entirety or in parts is prohibited. We rese [Truncated — 99,788 characters total]

TOOL CALL 2: Github Get Content [OK, 1560 ms] Getting content from sandhyatenneti/poc-power-plant owner: sandhyatenneti repo: poc-power-plant path: profile/extracted/Manuals__ID_Fan_O_M_Manual.txt Result preview: File: Manuals__ID_Fan_O_M_Manual.txt in sandhyatenneti/poc-power-plant Size: 88683 bytes URL: https://github.com/sandhyatenneti/poc-power-plant/blob/master/profile/extracted/Manuals__ID_Fan_O_M_Manual.txt Content: ``` SHANGHAI BLOWER WORKS CO., LTD. Phone: 086/021-56650577 Fax: 086/021-56651514 E-mail: design@sbw-cn.com COMPONENT MANUAL FOR INDUCED DRAUGHT FANS (ID-FANS) Facility: ID-Fan (2x660 MW unit) Power plant: FGD TIRODA Fan type: SAF36.5-19-2 Machine No. : Year of con [Truncated — 88,700 characters total]

### Maintenance Recommendation Based on Observed Operating Parameters

One-sentence answer: Nothing in the corpus currently requires a trip-level intervention — all measured temperatures and vibrations sit well below the 90°C/120°C and 4.5/11 mm/s OEM set points — but three real, repeatable findings from this conversation justify condition-based checks now, ahead of the standard preventive schedule: FD-A's motor drive-end bearing running consistently hotter than its fan drive-end bearing, FD-A's DE RTD elements showing a spread that suggests a sensor calibration check, and ID Fan B drawing meaningfully more current than ID Fan A at matched full load.

#### Table 1 — Findings and recommended actions (mapped to OEM manual references)

| Finding (from this conversation) | Observed value | Manual reference | Assessed severity | Recommended action | Maintenance interval per manual |
| --- | --- | --- | --- | --- | --- |
| FD-A motor DE bearing runs hotter than fan DE bearing | 62.2°C vs 56.4°C (+5.8°C, above RTD noise) | FD Manual §5.2.2 "Daily: control of bearing temperature"; §4.4.3 supervision table (alarm >90°C) | Watch — below alarm, but a real, consistent gap | Trend the motor DE bearing daily; check oil-cooling flow to that bearing at next scheduled check; verify no early bearing wear signs | Daily temp check; oil change every 4,000 hrs |
| FD-A DE RTD element spread (2.9°C) exceeds its own DE-vs-NDE difference | Elements 58.0/56.1/55.1°C | FD Manual §2.9.5.1 — 3 thermal resistances per bearing, each independently wired | Instrumentation finding, not a machine condition | Cross-check/calibrate the three DE RTD elements on FD-A; do not act on DE-vs-NDE comparisons until resolved | No fixed interval specified — treat as an out-of-cycle instrument check |
| ID Fan B draws more current than ID Fan A at matched full load | 156.6 A vs 143.1 A (+13.5 A, ~9%) at highest April MW bucket | ID Manual §3.2 maintenance plan — "Check for smoothly running per DIN ISO 10816" (daily), "Check blade fixation screws" (half-yearly) | Watch — current gap widens with load, current is corroborating only | At next outage, check ID-B's blade/vane alignment and DP against ID-A's; verify no partial blade fouling or misalignment | Blade visual check every 4,000 hrs per DIN ISO 10816 (daily smooth-running check) |
| June unit-down window: ID-B current, NDE temp, and motor bearing temps are dead/constant channels | Current 5.29 A constant, NDE temp ~0°C, motor bearings -0.285°C constant | ID Manual §2.5.2 — double hot-resistance (PT100) wiring allows spare-sensor swap | Instrumentation fault, unrelated to machine condition | Flag for sensor/wiring inspection on ID-B (use the spare RTD element per the double-resistance design) — separate from any operating recommendation | Not usage-based; corrective as found |

#### Table 2 — Standard preventive schedule already applicable to all fans (from both O&M manuals, for reference)

| Task | FD interval | ID interval |
| --- | --- | --- |
| Bearing temperature check | Daily | Daily |
| Oil level / pressure check | Daily | Daily |
| Vibration check (DIN ISO 10816 / VDI 2056) | Weekly | Daily |
| Filter check/clean | Weekly | Weekly |
| Oil change (with tank cleaning) | Every 4,000 hrs or 2 years | Every 4,000 hrs or 2 years |
| Blade visual check / fixation torque | Every 4,000 hrs | Every 4,000 hrs |
| Full bearing/blade overhaul | Every 16,000 hrs | Every 3 years or 24,000 hrs (whichever first), by SBW-trained staff |

#### Caveats

No threshold in this corpus is currently being approached — every measured max/avg discussed in this conversation is well under the 90°C bearing alarm and 4.5 mm/s vibration alarm. These are *watch* items, not trip-risk items.

This is a screening dataset, not a continuous trend — 3-4 day historian exports across three months (FD: Dec 2018; ID: Apr/Jun/Jul 2018). None of these findings can be confirmed as *progressive degradation* without a longer continuous record; they're presented as points worth checking at the next scheduled inspection, not emergency actions.

FD-A's DE-vs-NDE and DE-RTD-spread findings are instrument-level, not confirmed machine-condition findings — per the corpus's own rule, sensor faults must be screened separately from real machine condition. I have not folded the RTD spread into any temperature reading used for a maintenance decision.

ID-B's higher current is corroborating only (current is single-phase, CT-scaled, not comparable in absolute terms between machines) — it should prompt a physical blade/vane/DP check, not be treated alone as proof of a fault.

No vibration or DE/NDE bearing data was queried for the ID fans or PA fans in this conversation — the ID/PA maintenance recommendations above are limited to what current and count comparisons support; a full limit-screening pass (max/p95 vs §6 limits, per the corpus's stated method) across ID vibration and bearing temperature has not been run and would strengthen or rule out the ID-B finding.

Recommendations reference OEM manual sections directly (FD: Manuals__Instruction_Manual_For_FD_Fan.txt; ID: Manuals__ID_Fan_O_M_Manual.txt); PA fan's manual has not been pulled in this turn — if a PA-specific recommendation is needed, that manual (Manuals__Instruction_Manual_for_PA_Fan.txt) should be read first.

#### Chart

Bottom line: No fan needs an emergency shutdown or trip-level action based on the operating parameters reviewed in this conversation. The single clearest, actionable item is FD-A's motor drive-end bearing running a consistent 5.8°C above its own fan drive-end bearing — worth a targeted oil-cooling and lubrication check at the next scheduled inspection, alongside an RTD calibration check on FD-A's DE elements and a blade/vane alignment check on ID Fan B. Everything else falls within the standard preventive maintenance schedule already defined in the OEM manuals.

stop_reason: end_turn | tokens: {'input_tokens': 196051, 'output_tokens': 4564, 'cache_read_tokens': 48097, 'cache_creation_tokens': 0, 'total_tokens': 200615, 'model_call_count': 2}

# Q11.  Show relationship between FD Fan Current and FD Fan Bearing Temperature.

Asked: 2026-08-11T08:57:25.527951+00:00

ForgeAI Response

TOOL CALL 1: Forgeai Get Dataset Schema [FAILED, 75 ms] Getting schema for dataset 0 from source 665 source_id: 665 dataset_id: 0 Result preview: Error executing tool forgeai_get_dataset_schema: 1 validation error for forgeai_get_dataset_schemaArguments dataset_id Input should be greater than or equal to 1 [type=greater_than_equal, input_value=0, input_type=int] For further information visit https://errors.pydantic.dev/2.13/v/greater_than_equal

TOOL CALL 2: Forgeai Get Source Datasets [OK, 346 ms] Getting datasets for ForgeAI source 665 source_id: 665 search_word: chart1_fdfan1 Result preview: Dataset ID; Dataset Name; Schema Name; Dataset Type ID; Dataset Type; Dataset Path; Row Count Estimate; Data Volume Bytes; .... 3402219; chart1_fdfan1; fd_fan_data; 1; TABLE; 4299; .... Showing 1 of 1 row(s) returned. (Total Datasets: 1 ¦ Page: 1 ¦ Page Size: 10 ¦ Total Pages: 1)

TOOL CALL 3: Forgeai Get Dataset Schema [OK, 437 ms] Getting schema for dataset 3402219 from source 665 source_id: 665 dataset_id: 3402219 Result preview: Column ID; Column Name; Column Type. 14471; id; integer. 14472; row_seq; integer. 14473; reading_time_raw; string. 14474; reading_time; timestamp. 14475; furnace_lf_sd_olt_sa_flow; double. 14476; furnace_rt_sd_olt_sa_flow; double. Showing 6 of 73 row(s) returned.

TOOL CALL 4: Forgeai Get Dataset Column Profiles [OK, 692 ms] source_id: 665 dataset_id: 3402219 Result preview: Dataset Row Count: 4299 Dataset Column Count: 71 Column Name¦Column Type¦Description¦Desc Source¦Distinct Count¦Nulls¦Non-Nulls¦Unique¦Min Value¦Max Value¦Avg Value¦Avg Length¦Min Length¦Max Length¦Most Frequent Values With Count (Up to 5)¦Least Frequent Values With Count (Up to 5)¦Tags¦DQ Issues count id¦integer¦Unique identifier for each row, ensuring traceability and supporting data integrity in analysis.¦AI Generated¦4299¦0¦4299¦No¦1¦4299¦2150.0¦¦¦¦26 (1), 29 (1), 474 (1), 964 (1), 1677 (1)¦26 (1), 29 (1), 474 (1), 964 (1), 1677 (1)¦¦0 row_seq¦integer¦Sequential row number, providing an additional index for data ordering or troubleshooting.¦AI Generated¦4299¦0¦4299¦No¦1¦4299¦2150.0¦¦¦¦14 [Truncated — 26,014 characters total]

TOOL CALL 5: Forgeai Execute [OK, 406 ms] source_id: 665 query: WITH base AS ( SELECT reading_time, fdf_a_motor_current AS a_current, (fdf_a_brg1_temp_1+fdf_a_brg1_temp_2+fdf_a_brg1_temp_3)/3.0 AS a_de_temp, (fdf_a_brg3_temp_1+fdf_a_brg3_temp_2+fdf_a_brg3_temp_3)/3. … row_limit: 10 Result preview: n:20; avg_a_current:701; avg_a_de_temp:701; avg_a_nde_temp:701; avg_b_current:701; avg_b_de_temp:701; avg_b_nde_temp:701; a_de_corr_same:701; .... 4299; 47.25466008685818; 56.400807053989276; 56.13804981924456; 53.04417231314302; 48.1320795912305; 50.41149731023497; 0.24682777699856245; .... 1 row; .... Showing 2 of 2 row(s) returned.

TOOL CALL 6: Forgeai Execute [OK, 344 ms] source_id: 665 query: WITH base AS ( SELECT reading_time, fdf_a_motor_current AS a_current, (fdf_a_brg1_temp_1+fdf_a_brg1_temp_2+fdf_a_brg1_temp_3)/3.0 AS a_de_temp, fdf_b_motor_current AS b_current, (fdf_b_brg1_temp_1+f … row_limit: 20 Result preview: ERROR[READ_ONLY_VIOLATION]: Only SELECT/WITH/EXPLAIN statements are permitted (got Union). query: WITH base AS ( SELECT reading_time, fdf_a_motor_current AS a_current, (fdf_a_brg1_temp_1+fdf_a_brg1_temp_2+fdf_a_brg1_temp_3)/3.0 AS a_de_temp, fdf_b_motor_current AS b_current, (fdf_b_brg1_temp_1+fdf_b_brg1_temp_2+fdf_b_brg1_temp_3)/3.0 AS b_de_temp FROM fd_fan_data.chart1_fdfan1 ), bucketed AS ( SELECT *, ntile(4) OVER (ORDER BY a_current) AS a_bucket, ntile(4) OVER (ORDER BY b_current) AS b_bucket FROM base ) SELECT 'A' AS fan, a_bucket AS bucket, count(*) AS n, min(a_current) AS min_current, max(a_current) AS max_current, avg(a_current) AS avg_current, [Truncated — 1,006 characters total]

Need to wrap the union in an outer CTE per the query-limit rule.

TOOL CALL 7: Forgeai Execute [OK, 341 ms] source_id: 665 query: WITH base AS ( SELECT reading_time, fdf_a_motor_current AS a_current, (fdf_a_brg1_temp_1+fdf_a_brg1_temp_2+fdf_a_brg1_temp_3)/3.0 AS a_de_temp, fdf_b_motor_current AS b_current, (fdf_b_brg1_temp_1+f … row_limit: 20 Result preview: fan:25; bucket:23; n:20; min_current:701; max_current:701; avg_current:701; avg_de_temp:701. A; 1; 1075; 45.0668945; 46.1611328; 45.88605595525581; 55.98767656068213. A; 2; 1075; 46.1611328; 47.5214844; 46.749513912279056; 56.12226199975199. A; 3; 1075; 47.5214844; 47.97754; 47.781183559627905; 57.0198313378915. A; 4; 1074; 47.97754; 50.00244; 48.60314132141528; 56.47352596312854. B; 1; 1075; 47.6777344; 48.5048828; 48.148567766232574; 47.40816840496122. B; 2; 1075; 48.5048828; 54.9306641; 51.25887300102328; 48.17379405271319. Showing 6 of 9 row(s) returned.

### Relationship: FD Fan Motor Current vs Bearing Temperature

Headline: current explains only a weak-to-moderate part of bearing temperature variation for both FD fans — and for Fan A, ambient inlet-air temperature explains far more of it than current does.

Source: Power_Plant (source_id 665), table fd_fan_data.chart1_fdfan1, 4,299 rows, 23–26 Dec 2018 (FD-A and FD-B). "Bearing temperature" below is the fan drive-end (DE) — the average of the three brg1_temp_* RTD elements per fan.

#### Table 1 — Correlation summary (average metrics, whole window)

| Fan | Avg motor current (A) | Avg DE temp (°C) | Corr(current, DE temp) — same time | Corr(current, DE temp) — current lagged 15–30 min | Corr(inlet air temp, DE temp) | Corr(vane position, DE temp) |
| --- | --- | --- | --- | --- | --- | --- |
| FD-A | 47.3 | 58.0 | 0.25 (weak) | 0.29 (weak) | 0.87 (very strong) | 0.32 (weak) |
| FD-B | 53.0 | 47.7 | 0.40 (moderate) | 0.44 (moderate) | 0.94 (very strong) | 0.42 (moderate) |

FD-A: current only weakly relates to bearing temperature (0.25, rising slightly to 0.29 with a 15–30 min lag to allow for thermal lag). Inlet air temperature is a far stronger driver (0.87) — most of FD-A's DE temperature swing is explained by ambient/process air temperature, not motor loading.

FD-B: the current relationship is stronger (0.40–0.44, moderate) but inlet air temperature is still the dominant factor (0.94).

#### Table 2 — Bearing temp by current quartile (average metrics)

| Fan | Bucket | Current range (A) | Avg current (A) | Avg DE temp (°C) |
| --- | --- | --- | --- | --- |
| FD-A | Q1 (lowest) | 45.1–46.2 | 45.9 | 56.0 |
| FD-A | Q2 | 46.2–47.5 | 46.7 | 56.1 |
| FD-A | Q3 | 47.5–48.0 | 47.8 | 57.0 |
| FD-A | Q4 (highest) | 48.0–50.0 | 48.6 | 56.5 |
| FD-B | Q1 (lowest) | 47.7–48.5 | 48.1 | 47.4 |
| FD-B | Q2 | 48.5–54.9 | 51.3 | 48.2 |
| FD-B | Q3 | 54.9–56.4 | 55.7 | 47.4 |
| FD-B | Q4 (highest) | 56.4–58.6 | 57.1 | 49.5 |

FD-A's DE temp does not rise monotonically with current (highest at Q3, not Q4) — the shape is flat/inconsistent, consistent with the weak correlation. FD-B is closer to monotonic (Q4 highest) but still not clean.

#### Caveats

RTD spread caveat (this matters here): the three DE RTD elements on FD-A read an average spread of about 2.9 °C (57.97 / 56.12 / 55.12 °C) between elements — larger than the ~1.0 °C difference between FD-A's current quartiles in Table 2. That means FD-A's current-vs-temperature signal is within sensor noise and not resolvable from this data. FD-B's RTD spread is smaller (~0.7–0.9 °C among its three elements), so its 2.1 °C spread across current quartiles is a more credible (though still moderate) signal.

Confounder was tested with a query, not assumed: inlet air temperature correlates 0.87 (A) and 0.94 (B) with DE temp, i.e. far stronger than current — ambient/process air temperature is the primary driver of bearing temperature in this window, not motor loading.

This is a 3-day historian chart export (23–26 Dec 2018), not a continuous trend — treat this as a screening result, not a degradation record.

All temperatures are well below the 90 °C alarm / 120 °C trip set points (OEM manual); no action needed on this basis.

#### Chart

Bottom line: current is not a reliable predictor of FD bearing temperature in this window — for FD-A the apparent relationship is smaller than the sensor's own RTD spread and should not be acted on; for FD-B it is a moderate, more credible relationship, but ambient inlet-air temperature is the stronger driver for both fans. No thresholds are being approached, so no maintenance action is indicated from this alone.

stop_reason: end_turn | tokens: {'input_tokens': 412366, 'output_tokens': 10579, 'cache_read_tokens': 289752, 'cache_creation_tokens': 0, 'total_tokens': 422945, 'model_call_count': 7}

# Q12.  How did FD Fan Bearing Temperature differ from FD Fan Motor Bearing at drive end and non-drive end?

Asked: 2026-08-11T09:03:10.568937+00:00

ForgeAI Response

TOOL CALL 1: Forgeai Get Dataset Schema [OK, 338 ms] Getting schema for dataset 1 from source 665 source_id: 665 dataset_id: 1 Result preview: Error getting dataset schema: ForgeAI API error: {'error': 'Dataset schema not found'} (Status: 404)

TOOL CALL 2: Forgeai Get Source Datasets [OK, 345 ms] Getting datasets for ForgeAI source 665 source_id: 665 search_word: chart1_fdfan1 Result preview: Dataset ID; Dataset Name; Schema Name; Dataset Type ID; Dataset Type; Dataset Path; Row Count Estimate; Data Volume Bytes; .... 3402219; chart1_fdfan1; fd_fan_data; 1; TABLE; 4299; .... Showing 1 of 1 row(s) returned. (Total Datasets: 1 ¦ Page: 1 ¦ Page Size: 10 ¦ Total Pages: 1)

TOOL CALL 3: Forgeai Get Dataset Schema [OK, 320 ms] Getting schema for dataset 3402219 from source 665 source_id: 665 dataset_id: 3402219 Result preview: Column ID; Column Name; Column Type. 14471; id; integer. 14472; row_seq; integer. 14473; reading_time_raw; string. 14474; reading_time; timestamp. 14475; furnace_lf_sd_olt_sa_flow; double. 14476; furnace_rt_sd_olt_sa_flow; double. Showing 6 of 73 row(s) returned.

TOOL CALL 4: Forgeai Execute [OK, 358 ms] source_id: 665 query: SELECT avg(fdf_a_brg1_temp_1) AS a_de_e1, avg(fdf_a_brg1_temp_2) AS a_de_e2, avg(fdf_a_brg1_temp_3) AS a_de_e3, avg((fdf_a_brg1_temp_1+fdf_a_brg1_temp_2+fdf_a_brg1_temp_3)/3.0) AS a_de_avg, avg(fdf_a_brg3_temp_1) A … hive_execution_engine: hive_thrift Result preview: a_de_e1:701; a_de_e2:701; a_de_e3:701; a_de_avg:701; a_nde_e1:701; a_nde_e2:701; a_nde_e3:701; a_nde_avg:701; .... 57.97054903354277; 56.115122287741286; 55.11674984068361; 56.400807053989276; 55.716531347173856; 55.69868947315677; 56.998928637404276; 56.13804981924456; .... 1 row; .... Showing 2 of 2 row(s) returned.

### FD Fan Bearing Temperature: Fan vs Motor, Drive End and Non-Drive End

One-sentence answer: On FD-A the fan and motor run close together at the non-drive end (57.4°C vs 56.1°C, +1.3°C) but the motor is noticeably hotter than the fan at the drive end (62.2°C vs 56.4°C, +5.8°C); on FD-B the picture reverses at the drive end — motor is again hotter than fan (52.9°C vs 48.1°C, +4.8°C) — while at the non-drive end the fan is marginally hotter than the motor (50.4°C vs 49.1°C, +1.3°C).

Source: Power_Plant (source_id 665), table fd_fan_data.chart1_fdfan1, 23–26 Dec 2018. DE (drive end) = fan brg1_temp_* (3-element average) vs motor motor_brg2_temp (single element, per corpus convention — motor numbering runs opposite to fan numbering). NDE (non-drive end) = fan brg3_temp_* (3-element average) vs motor motor_brg1_temp. All 4,299 rows in the table passed the non-physical-value filter (temp > 0) — no dead channels in this window.

#### Table 1 — Average bearing temperatures (°C)

| Fan | Fan DE (avg 3 RTDs) | Fan NDE (avg 3 RTDs) | Motor DE | Motor NDE | Motor DE − Fan DE | Motor NDE − Fan NDE | Fan DE − Fan NDE |
| --- | --- | --- | --- | --- | --- | --- | --- |
| FD-A | 56.4 | 56.1 | 62.2 | 57.4 | +5.8 | +1.3 | +0.3 |
| FD-B | 48.1 | 50.4 | 52.9 | 49.1 | +4.8 | −1.3 | −2.3 |

(Negative in the last two columns means the second-named value is larger — e.g. FD-B's fan NDE, 50.4°C, is 2.3°C *hotter* than its fan DE, 48.1°C; FD-B's fan NDE is also 1.3°C hotter than its motor NDE.)

#### Table 2 — RTD element spread at each fan location (°C)

| Fan | DE elements (1/2/3) | DE spread | NDE elements (1/2/3) | NDE spread |
| --- | --- | --- | --- | --- |
| FD-A | 58.0 / 56.1 / 55.1 | 2.9 | 55.7 / 55.7 / 57.0 | 1.3 |
| FD-B | 47.7 / 48.4 / 48.2 | 0.7 | 51.6 / 49.4 / 50.3 | 2.2 |

#### Caveats

FD-A fan DE-vs-NDE difference (0.3°C) is not resolvable — it is far smaller than the 2.9°C spread among FD-A's own DE RTD elements. Don't read this as "DE runs hotter than NDE" on FD-A; it's within sensor noise.

FD-A motor-vs-fan gaps (5.8°C at DE, 1.3°C at NDE) are real — both exceed the relevant RTD spreads, so the motor genuinely running hotter than the fan at the drive end is a credible finding, not noise. Note the motor bearings are each a single element (no internal spread check possible for the motor side).

FD-B's 2.3°C fan DE-vs-NDE gap is borderline — it's about the same size as FD-B's own NDE spread (2.2°C), so treat the "NDE runs hotter than DE" finding on FD-B as weak/marginal rather than solid, even though it points the opposite way from FD-A.

FD-B motor DE-vs-fan DE gap (4.8°C) is real (well above FD-B's 0.7°C DE spread); the motor-vs-fan NDE gap (1.3°C) is close to FD-B's 2.2°C NDE spread, so that one is also marginal.

All averages are well within OEM limits: alarm >90°C, trip >120°C (fan bearings, all three OEM manuals); rolling-bearing design limit ≤70°C normal / ≤80°C max; motor sliding bearings ≤80°C. Nothing here needs action.

This is a 3-day historian chart export, not a continuous trend — a screening sample only.

#### Chart

Bottom line: The motor drive-end bearing is the warmest point on both fans and runs meaningfully hotter than its own fan's DE bearing (FD-A +5.8°C, FD-B +4.8°C) — a consistent, above-noise pattern worth watching over time, though still far from the 90°C alarm. The fan-side DE-vs-NDE comparisons (both fans) are within or close to RTD element noise and shouldn't be treated as firm findings. No immediate action needed on any reading.

stop_reason: end_turn | tokens: {'input_tokens': 259922, 'output_tokens': 6399, 'cache_read_tokens': 193168, 'cache_creation_tokens': 0, 'total_tokens': 266321, 'model_call_count': 5}